## CoverSheet (hidden)
EDB Information Disclosure Requirements
Information Templates
for
Schedules 11a–13
| Company Name | Aurora Energy Limited
| Disclosure Date | 42094
| AMP Planning Period Start Date (first day) | 42095
Templates for Schedules 11a–13 (Asset Management Plan)
Template Version 3.0. Prepared 13 December 2013

## TOC (hidden)
Table of Contents
Schedule | Description
Asset Management Plan Schedule Templates
11a | Report on Forecast Capital Expenditure
11b | Report on Forecast Operational Expenditure
12a | Report on Asset Condition
12b | Report on Forecast Capacity
12c | Report on Forecast Demand
12d | Report on Forecast Interruptions and Duration
13 | Report on Asset Management Maturity

## Guidelines (hidden)
Disclosure Template Guidelines for Information Entry
These templates have been prepared for use by EDBs when making disclosures under subclauses 2.6.1(4), 2.6.1(5) and 2.6.5(5) of the Electricity Distribution Information Disclosure Determination 2012. Disclosures made under subclauses 2.6.1(4) and 2.6.1(5) must be made before the start of each disclosure year. Disclosures made under subclauses 2.6.5(5) must be made within 5 months after the start of the disclosure year. The information disclosed under 2.6.5(5) should be identical to that disclosed under 2.6.1(4) and 2.6.1(5).
Under clause 2.6.3, EDBs can elect to complete and publicly disclose before the start of the disclosure year, an AMP update. EDBs can elect to complete and publicly disclose an AMP update instead of a full AMP in the following years: • 31 March 2014 • 31 March 2015 If electing to complete an AMP update, EDBs can choose to not complete and disclose Schedule 13: Report on Asset Management Maturity Table. Schedule 13 sheet should be removed if not completed. If disclosing a Full AMP, EDBs must complete and disclose Schedule 13.
Company Name and Dates
To prepare the templates for disclosure, the supplier's company name should be entered in cell C8, the date of the first day of the 10 year planning period should be entered in cell C12, and the date on which the information is disclosed should be entered in cell C10 of the CoverSheet worksheet.
The cell C12 entry (planning period start date) is used to calculate disclosure years in the column headings that show above some of the tables. It is also used to calculate the AMP planning period dates in the template title blocks (the title blocks are the light green shaded areas at the top of each template). The cell C8 entry (company name ) is used in the template title blocks. Dates should be entered in day/month/year order (Example -"1 April 2013").
Data Entry Cells and Calculated Cells
Data entered into this workbook may be entered only into the data entry cells. Data entry cells are the bordered, unshaded areas (white cells) in each template. Under no circumstances should data be entered into the workbook outside a data entry cell. In some cases, where the information for disclosure is able to be ascertained from disclosures elsewhere in the workbook, such information is disclosed in a calculated cell. Under no circumstances should the formulas in a calculated cell be overwritten.
Validation Settings on Data Entry Cells
To maintain a consistency of format and to guard against errors in data entry, some data entry cells test entries for validity and accept only a limited range of values. For example, entries may be limited to a list of category names or to values between 0% and 100%. Where this occurs, a validation message will appear when data is being entered.
Conditional Formatting Settings on Data Entry Cells
Schedule 12a columns G to K contains conditional formatting. The cells will change colour if the row totals do not add to 100%.
Inserting Additional Rows
The templates for schedules 11a, 12b and 12c may require additional rows to be inserted in tables marked 'include additional rows if needed'. Additional rows must not be inserted directly above the first row or below the last row of a table. This is to ensure that entries made in the new row are included in the totals. For schedule 12b the formula for column J (Utilisation of Installed Firm Capacity %) will need to be copied into the inserted row(s).
Schedule 11a & 11b
Schedule 11a requires Capital and Operational Expenditure to be expressed in both nominal and constant prices. The differences between the nominal and constant prices should reflect EDB expectations of the impact of changes in the costs of its labour, materials and other inputs (ie, inflationary pressures).
Schedule 12b(ii)
The purpose of schedule 12b(ii) is to disclose transformer capacity as at the end of the current year. As the information may not be available in time for disclosures made under subclause 2.6.1(4), but available for disclosures made under 2.6.5(5), EDBs can choose not to disclose transformer capacity under schedule 12b(ii). EDBs who do not disclose transformer capacity under schedule 12b(ii) must disclose the information in schedule 9e(iii). Accordingly, the Excel template has been modified to allow the value "N/A" to be entered into these input cells.
Schedule 12d Report Forecast Interruptions and Duration sub-network disclosures
If the supplier has sub-networks, schedule 12d must be completed for the network and for each sub-network. A copy of the schedule 12d worksheet must be made for each sub-network.
Schedule 13 Report on Asset Management Maturity
The name of the standard applied (eg, 'PAS55') must be entered in cell K4.

## S11a.Capex Forecast
[13 empty] | Company Name | Aurora Energy Limited
[13 empty] | AMP Planning Period | 42095 -1409d mmmm yyyy –45747 -1409d mmmm yyyy
SCHEDULE 11a: REPORT ON FORECAST CAPITAL EXPENDITURE
This schedule requires a breakdown of forecast expenditure on assets for the current disclosure year and a 10 year planning period. The forecasts should be consistent with the supporting information set out in the AMP. The forecast is to be expressed in both constant price and nominal dollar terms. Also required is a forecast of the value of commissioned assets (i.e., the value of RAB additions) EDBs must provide explanatory comment on the difference between constant price and nominal dollar forecasts of expenditure on assets in Schedule 14a (Mandatory Explanatory Notes). This information is not part of audited disclosure information.
sch ref
7 | [5 empty] | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | CY+9 | CY+10
8 |  |  |  |  | for year ended | 2015-03-31 | 2016-03-31 | 2017-03-31 | 2018-03-31 | 2019-03-31 | 2020-03-31 | 2021-03-31 | 2022-03-31 | 2023-03-31 | 2024-03-31 | 2025-03-31
9 | 11a(i): Expenditure on Assets Forecast |  |  |  |  | 2015-03-31: $000 (in nominal dollars)
10 |  |  |  | Consumer connection |  | 5981.5 | 5558.5 | 5502 | 5502 | 5502 | 5502 | 5502 | 5502 | 5502 | 5502 | 5502
11 |  |  |  | System growth |  | 10296 | 12247.4875 | 12581.5125 | 8980.2 | 6912.5 | 4818.75 | 4450 | 3643.75 | 3125 | 2037.5 | 575
12 |  |  |  | Asset replacement and renewal |  | 10992.25 | 18789.5741 | 18322.2879 | 15449.7155 | 10144.675 | 8446 | 10081 | 9386 | 9003.5 | 8971 | 5243.5
13 |  |  |  | Asset relocations |  | 820.25 | 556.25 | 300 | 881.25 | 1075 | 1075 | 1075 | 1075 | 1075 | 1075 | 1075
14 |  |  |  | Reliability, safety and environment:
15 |  |  |  | Quality of supply |  | 1063 | 1187.125 | 1385.75 | 975 | 610.5 | 300.125 | 145 | 120 | 30 | 0 | 0
16 |  |  |  | Legislative and regulatory
17 |  |  |  | Other reliability, safety and environment |  | 438.5 | 690 | 466.875 | 237.5 | 165.625 | 165 | 131.25 | 120 | 120 | 120 | 120
18 |  |  |  | Total reliability, safety and environment |  | 1501.5 | 1877.125 | 1852.625 | 1212.5 | 776.125 | 465.125 | 276.25 | 240 | 150 | 120 | 120
19 |  |  | Expenditure on network assets |  |  | 29591.5 | 39028.9366 | 38558.4254 | 32025.6655 | 24410.3 | 20306.875 | 21384.25 | 19846.75 | 18855.5 | 17705.5 | 12515.5
20 |  |  |  | Non-network assets
21 |  |  | Expenditure on assets |  |  | 29591.5 | 39028.9366 | 38558.4254 | 32025.6655 | 24410.3 | 20306.875 | 21384.25 | 19846.75 | 18855.5 | 17705.5 | 12515.5
22
23 |  | plus |  | Cost of financing
24 |  | less |  | Value of capital contributions |  | 4187.05 | 3960.44 | 3961.44 | 4016.46 | 4071.48 | 4071.48 | 4071.48 | 4071.48 | 4071.48 | 4071.48 | 4071.48
25 |  | plus |  | Value of vested assets
26
27 |  |  | Capital expenditure forecast |  |  | 25404.45 | 35068.4966 | 34596.9854 | 28009.2055 | 20338.82 | 16235.395 | 17312.77 | 15775.27 | 14784.02 | 13634.02 | 8444.02
28
29 |  |  |  | Value of commissioned assets
30 | [5 empty] | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | CY+9 | CY+10
[5 empty] | for year ended | 2015-03-31 | 2016-03-31 | 2017-03-31 | 2018-03-31 | 2019-03-31 | 2020-03-31 | 2021-03-31 | 2022-03-31 | 2023-03-31 | 2024-03-31 | 2025-03-31
32 | [5 empty] | 2015-03-31: $000 (in constant prices)
33 |  |  |  | Consumer connection |  | 5982 | 5454 | 5389.0608 | 5281.4888 | 5178.0817 | 5076.9732 | 4978.4501 | 4880.8334 | 4785.1308 | 4691.3047 | 4599.3183 | from row 76
34 |  |  |  | System growth |  | 10296 | 12019.1241 | 11890.4382 | 7397.2374 | 6386.0876 | 4364.4945 | 4026.5545 | 3232.3767 | 2717.836 | 1737.2834 | 480.663 | from row 87
35 |  |  |  | Asset replacement and renewal |  | 10991.75 | 18439.2287 | 17009.5915 | 13852.8113 | 9372.1206 | 7649.8098 | 9121.7294 | 8326.3363 | 7830.4117 | 7649.1629 | 4383.229 | from row 101
36 |  |  |  | Asset relocations |  | 820.25 | 545.8783 | 288.3509 | 1012.9975 | 993.1348 | 973.6616 | 972.707 | 953.6343 | 934.9356 | 916.6035 | 898.6309 | from row 113
37 |  |  |  | Reliability, safety and environment:
38 |  |  |  | Quality of supply |  | 1063 | 1164.9902 | 1382.6426 | 773.1762 | 564.0082 | 271.8327 | 131.2023 | 106.4522 | 26.0912 | 0 | 0 | from row 126
39 |  |  |  | Legislative and regulatory |  | 2015-03-31: 0; 2016-03-31: 0; 2017-03-31: 0; 2018-03-31: 0; 2019-03-31: 0; 2020-03-31: 0 | from row 139
40 |  |  |  | Other reliability, safety and environment |  | 438.5 | 677 | 429 | 158 | 153 | 150 | 118.7607 | 106.4522 | 104.3649 | 102.3185 | 100.3123 | from row 154
41 |  |  |  | Total reliability, safety and environment |  | 1501.5 | 1841.9902 | 1811.6426 | 931.1762 | 717.0082 | 421.8327 | 249.9631 | 212.9044 | 130.4561 | 102.3185 | 100.3123
42 |  |  | Expenditure on network assets |  |  | 29591.5 | 38300.2214 | 36389.084 | 28475.7112 | 22646.4329 | 18486.7718 | 19349.4041 | 17606.0852 | 16398.7702 | 15096.6731 | 10462.1535
43 |  |  |  | Non-network assets |  | 2015-03-31: 0; 2016-03-31: 0; 2017-03-31: 0; 2018-03-31: 0; 2019-03-31: 0; 2020-03-31: 0 | from row 182
44 |  |  | Expenditure on assets |  |  | 29591.5 | 38300.2214 | 36389.084 | 28475.7112 | 22646.4329 | 18486.7718 | 19349.4041 | 17606.0852 | 16398.7702 | 15096.6731 | 10462.1535
45
46 |  | Subcomponents of expenditure on assets (where known)
47 |  |  |  | Energy efficiency and demand side management, reduction of energy losses
48 |  |  |  | Overhead to underground conversion
49 |  |  |  | Research and development
57 | [5 empty] | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | CY+9 | CY+10
58 |  |  |  |  | for year ended | 2015-03-31 | 2016-03-31 | 2017-03-31 | 2018-03-31 | 2019-03-31 | 2020-03-31 | 2021-03-31 | 2022-03-31 | 2023-03-31 | 2024-03-31 | 2025-03-31
59 |  | Difference between nominal and constant price forecasts |  |  |  | 2015-03-31: $000
60 |  |  |  | Consumer connection |  | -0.5 | 104.5 | 112.9392 | 220.5112 | 323.9183 | 425.0268 | 523.5499 | 621.1666 | 716.8692 | 810.6953 | 902.6817
61 |  |  |  | System growth |  | 0 | 228.3634 | 691.0743 | 1582.9626 | 526.4124 | 454.2555 | 423.4455 | 411.3733 | 407.164 | 300.2166 | 94.337
62 |  |  |  | Asset replacement and renewal |  | 0.5 | 350.3453 | 1312.6963 | 1596.9042 | 772.5544 | 796.1902 | 959.2706 | 1059.6637 | 1173.0883 | 1321.8371 | 860.271
63 |  |  |  | Asset relocations |  | 0 | 10.3717 | 11.6491 | -131.7475 | 81.8652 | 101.3384 | 102.293 | 121.3657 | 140.0644 | 158.3965 | 176.3691
64 |  |  |  | Reliability, safety and environment:
65 |  |  |  | Quality of supply |  | 0 | 22.1348 | 3.1074 | 201.8238 | 46.4918 | 28.2923 | 13.7977 | 13.5478 | 3.9088 | 0 | 0
66 |  |  |  | Legislative and regulatory |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 |  |  |  | Other reliability, safety and environment |  | 0 | 13 | 37.875 | 79.5 | 12.625 | 15 | 12.4893 | 13.5478 | 15.6351 | 17.6815 | 19.6877
68 |  |  |  | Total reliability, safety and environment |  | 0 | 35.1348 | 40.9824 | 281.3238 | 59.1168 | 43.2923 | 26.2869 | 27.0956 | 19.5439 | 17.6815 | 19.6877
69 |  |  | Expenditure on network assets |  |  | 0 | 728.7152 | 2169.3414 | 3549.9543 | 1763.8671 | 1820.1032 | 2034.8459 | 2240.6648 | 2456.7298 | 2608.8269 | 2053.3465
70 |  |  |  | Non-network assets |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 |  |  | Expenditure on assets |  |  | 0 | 728.7152 | 2169.3414 | 3549.9543 | 1763.8671 | 1820.1032 | 2034.8459 | 2240.6648 | 2456.7298 | 2608.8269 | 2053.3465
72 | [5 empty] | 2015-03-31: Current Year CY
73 | [5 empty] | 2016-03-31: CY+1; 2017-03-31: CY+2; 2018-03-31: CY+3; 2019-03-31: CY+4; 2020-03-31: CY+5
74 | 11a(ii): Consumer Connection |  |  |  | for year ended | 2015-03-31 | 2016-03-31 | 2017-03-31 | 2018-03-31 | 2019-03-31 | 2020-03-31
75 |  |  |  | Consumer types defined by EDB* |  | 2015-03-31: $000 (in constant prices)
76 |  |  |  | Load group 0 (1 kVA un-metered) |  | 23 | 16 | 12.2918 | 11.512 | 11.2771 | 10.9891
77 |  |  |  | Load group 0A (2 kVA un-metered) |  | 0 | 0 | 0 | 0 | 0 | 0
78 |  |  |  | Load group 1A (8 kVA, plus standard domestic 8 kVA) |  | 56 | 14 | 12.4469 | 11.6182 | 11.2939 | 10.9841
|  |  |  | Load group 1 (15 kVA, plus standard domestic 15 kVA) |  | 621 | 3165 | 2996.9799 | 2952 | 2861 | 2841
|  |  |  | Load group 2 (16 - 149 kVA) |  | 2498 | 972 | 965.8005 | 940 | 972 | 981
|  |  |  | Load group 3 (150 - 249 kVA) |  | 746 | 368 | 450 | 512 | 513 | 446
|  |  |  | Load group 3A (250 - 499 kVA) |  | 715 | 228 | 279 | 250 | 215 | 195
79 |  |  |  | Load group 4 (500 - 2,499 kVA) |  | 1323 | 448 | 495.1883 | 456.6245 | 450.0918 | 450
80 |  |  |  | Load group 5 (2,500+ kVA) |  | 0 | 243 | 177.3534 | 147.734 | 144.4188 | 142
81 |  |  |  | *include additional rows if needed
82 |  |  | Consumer connection expenditure |  |  | 5982 | 5454 | 5389.0608 | 5281.4888 | 5178.0817 | 5076.9732 | [5 empty] | to row 33
83 |  | less |  | Capital contributions funding consumer connection |  | 3653.8875 | 3605.6191 | 3774.0119 | 3358.0116 | 3425.9424 | 3438.6
84 |  |  | Consumer connection less capital contributions |  |  | 2328.1125 | 1848.3809 | 1615.0489 | 1923.4771 | 1752.1393 | 1638.3732
85 | 11a(iii): System Growth
86 |  |  |  | Subtransmission |  | 550 | 1351.3248 | 1509.0364 | 0 | 692.8847 | 1585.0304
87 |  |  |  | Zone substations |  | 9124 | 10380.7532 | 9639.3787 | 7161.6566 | 5496.8856 | 2598.3178
88 |  |  |  | Distribution and LV lines |  | 336.5 | 90.7753 | 48.0585 | 47.1162 | 11.5481 | 0
89 |  |  |  | Distribution and LV cables |  | 112.5 |  | 396.0019 | 0 | 0 | 0
90 |  |  |  | Distribution substations and transformers |  | 173 | 196.2709 | 192.2339 | 188.4646 | 184.7693 | 181.1463
91 |  |  |  | Distribution switchgear |  |  |  | 105.7287 | 0 | 0 | 0
92 |  |  |  | Other network assets
93 |  |  | System growth expenditure |  |  | 10296 | 12019.1241 | 11890.4382 | 7397.2374 | 6386.0876 | 4364.4945 | [5 empty] | to row 34
94 |  | less |  | Capital contributions funding system growth
95 |  |  | System growth less capital contributions |  |  | 10296 | 12019.1241 | 11890.4382 | 7397.2374 | 6386.0876 | 4364.4945
103 | [5 empty] | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5
104 |  |  |  |  | for year ended | 2015-03-31 | 2016-03-31 | 2017-03-31 | 2018-03-31 | 2019-03-31 | 2020-03-31
105 | 11a(iv): Asset Replacement and Renewal |  |  |  |  | 2015-03-31: $000 (in constant prices)
106 |  |  |  | Subtransmission |  | 946 | 2353.2376 | 673.1667 | 3580.8283 | 2928.5928 | 3095.338
107 |  |  |  | Zone substations |  | 880 | 2833.6605 | 5046.141 | 2544.2727 | 1455.0579 | 441.5442
108 |  |  |  | Distribution and LV lines |  | 2578.5 | 4170.7556 | 4084.9712 | 4146.2223 | 3372.039 | 3147.4176
109 |  |  |  | Distribution and LV cables |  | 37.5 | 160.4514 | 198.001 | 194.1186 | 176.4546 | 168.4661
110 |  |  |  | Distribution substations and transformers |  | 929.5 | 915.1129 | 692.0422 | 678.4727 | 665.1693 | 652.1268
111 |  |  |  | Distribution switchgear |  | 338.5 | 210.9912 | 153.7872 | 150.7717 | 147.8154 | 144.9171
112 |  |  |  | Other network assets |  | 5281.75 | 7795.0196 | 6161.4823 | 2558.1249 | 626.9914 | 0
113 |  |  | Asset replacement and renewal expenditure |  |  | 10991.75 | 18439.2287 | 17009.5915 | 13852.8113 | 9372.1206 | 7649.8098 | [5 empty] | to row 35
114 |  | less |  | Capital contributions funding asset replacement and renewal
115 |  |  | Asset replacement and renewal less capital contributions |  |  | 10991.75 | 18439.2287 | 17009.5915 | 13852.8113 | 9372.1206 | 7649.8098
116 | 11a(v):Asset Relocations
117 |  |  |  | Project or programme*
118 |  |  |  | Chorus changeovers |  |  | 245.3386 | 240.2924 | 0 | 0 | 0
119 |  |  |  | OH to UG Conversion CODC Area |  | 132.0975 | 24.5339 | 0 | 94.2323 | 92.3846 | 90.5732
120 |  |  |  | OH to UG Conversion Dunedin Area |  | 340.6725 | 147.2031 | 0 | 565.3939 | 554.3078 | 543.439
121 |  |  |  | OH to UG Conversion QLDC Area |  | 222.48 | 128.8027 | 48.0585 | 353.3712 | 346.4424 | 339.6494
122 |  |  |  | LTSA Roading Work |  | 2015-03-31: 125
123 |  |  |  | *include additional rows if needed
124 |  |  |  | All other asset relocations projects or programmes
125 |  |  | Asset relocations expenditure |  |  | 820.25 | 545.8783 | 288.3509 | 1012.9975 | 993.1348 | 973.6616 | [5 empty] | to row 36
126 |  | less |  | Capital contributions funding asset relocations |  | 533.1625 | 354.8209 | 187.4281 | 658.4484 | 645.5376 | 632.88
127 |  |  | Asset relocations less capital contributions |  |  | 287.0875 | 191.0574 | 100.9228 | 354.5491 | 347.5972 | 340.7815
128
129 | 11a(vi):Quality of Supply
130 |  |  |  | Project or programme*
131 |  |  |  | AB9 - Recloser at Tomahawk |  | 13 |  |  | 0 | 0 | 0
|  |  |  | AX168 - Recloser on Dunstan Rd spur |  | 13 |  |  | 0 | 0 | 0
|  |  |  | AX168 - Recloser on Letts Gully spur |  |  | 12.2669 |  | 0 | 0 | 0
|  |  |  | CE195 - Recloser on Springvale Road spur |  | 13 |  |  | 0 | 0 | 0
|  |  |  | Complete 11kV Ring Ardgour Valley |  |  | 73.6016 |  | 0 | 0 | 0
|  |  |  | intertie between QT5232 & QT5242 |  | 18 |  |  | 0 | 48.5019 | 15.8503
|  |  |  | Fire Security and Seismic |  | 25 |  |  | 0 | 0 | 0
|  |  |  | Ettrick - Recloser on Timaburn Road spur |  |  | 12.2669 |  | 0 | 0 | 0
|  |  |  | Fire , Security, Earthquake & Asbestos Upgrades |  |  | 0 | 192.2339 | 188.4646 | 184.7693 | 45.2866
|  |  |  | Install 33kV circuit breaker at CYD-Earnscleugh Substation |  | 3 | 7.3602 | 86.5053 | 0 | 0 | 0
|  |  |  | Install 33kV circuit breaker at Dalefield zone substation |  | 45 | 24.5339 |  | 0 | 0 | 0
|  |  |  | Install 33kV circuit breaker at Ettrick zone substation |  | 20 | 29.4406 |  | 0 | 0 | 0
|  |  |  | Install 33kV circuit breaker at Omakau zone substation |  | 3 |  |  | 0 | 0 | 0
|  |  |  | Install heatpump/condensation removal |  |  | 36.8008 |  | 0 | 0 | 0
|  |  |  | Install HV tie between WK2752 and 2756 |  |  | 147.2031 |  | 0 | 103.9327 | 33.9649
|  |  |  | Install new HV feeder in CML to Leitrum St |  | 70 | 0 | 0 | 0 | 0 | 81.5159
|  |  |  | Installl 33kV circuit breaker at Remarkables zone substation |  | 25 | 76.055 |  | 0 | 0 | 0
|  |  |  | Marsh Road |  | 31 |  |  | 0 | 0 | 0
|  |  |  | Maungawera Supply |  | 192 |  |  | 0 | 0 | 0
|  |  |  | Omakau Fans |  | 2015-03-31: 25
|  |  |  | Queenstown 33 kV |  | 2015-03-31: 180
|  |  |  | Voltage Regulator |  | 135 |  |  | 0 | 0 | 0
|  |  |  | New line Huddleston Road |  |  | 73.6016 |  | 0 | 0 | 0
|  |  |  | No.8 replacement (Omakau area) |  |  | 36.8008 |  | 0 | 0 | 0
|  |  |  | Oil Cable Replacement |  | 2018-03-31: 0; 2019-03-31: 0; 2020-03-31: 0
|  |  |  | Poolburn Regulators |  |  | 73.6016 |  | 0 | 0 | 0
|  |  |  | Nee Wanaka Feeder 2751 |  | 220 |  |  | 0 | 0 | 0
|  |  |  | QT5202 - Recloser at Closeburn |  |  | 66.2414 |  | 0 | 0 | 0
|  |  |  | Reconfiguration of ET8 |  |  | 16.1923 |  | 62.1933 | 15.2435 | 0
|  |  |  | Reconfigure Lauder Regulators |  |  | 36.8008 |  | 0 | 0 | 0
|  |  |  | Replace transformer Buccholtz relays at Central zone subs |  | 6 | 19.6271 |  | 0 | 0 | 0
|  |  |  | Stage 1 Se+F152:H154ismic Works |  |  | 336.7272 | 49.0197 | 49.0008 | 12.01
132 |  |  |  | Stage 2 Seismic Works |  | 2017-03-31: 958.7668; 2018-03-31: 107.4248; 2019-03-31: 26.3296
133 |  |  |  | Stage 3 Seismic Works |  | 2018-03-31: 271.8603; 2019-03-31: 66.6324
134 |  |  |  | Stage 4 Seismic Works |  | 2019-03-31: 14.2041; 2020-03-31: 4.6419
135 |  |  |  | Underground Substation Improvement Programme |  | 26 | 85.8685 | 96.117 | 94.2323 | 92.3846 | 90.5732
136 |  |  |  | *include additional rows if needed
137 |  |  |  | All other quality of supply projects or programmes
138 |  |  | Quality of supply expenditure |  |  | 1063 | 1164.9902 | 1382.6426 | 773.1762 | 564.0082 | 271.8327 | [5 empty] | to row 38
139 |  | less |  | Capital contributions funding quality of supply
140 |  |  | Quality of supply less capital contributions |  |  | 1063 | 1164.9902 | 1382.6426 | 773.1762 | 564.0082 | 271.8327
141
142 | 11a(vii): Legislative and Regulatory
143 |  |  |  | Project or programme*
144 |  |  |  | [Description of material project or programme]
145 |  |  |  | [Description of material project or programme]
146 |  |  |  | [Description of material project or programme]
147 |  |  |  | [Description of material project or programme]
148 |  |  |  | [Description of material project or programme]
149 |  |  |  | *include additional rows if needed
150 |  |  |  | All other legislative and regulatory projects or programmes
151 |  |  | Legislative and regulatory expenditure |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | to row 39
152 |  | less |  | Capital contributions funding legislative and regulatory
153 |  |  | Legislative and regulatory less capital contributions |  |  | 0 | 0 | 0 | 0 | 0 | 0
161
162 | [5 empty] | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5
163 | 11a(viii): Other Reliability, Safety and Environment |  |  |  | for year ended | 2015-03-31 | 2016-03-31 | 2017-03-31 | 2018-03-31 | 2019-03-31 | 2020-03-31
164 |  |  |  | Project or programme* |  | 2015-03-31: $000 (in constant prices)
165 |  |  |  | Replace transformer Buccholtz relays at Dunedin zone subs |  | 2015-03-31: 7.5; 2016-03-31: 29
|  |  |  | Replacement of oil-filled switchgear |  | 20 | 324 | 384 | 113 | 111 | 109
|  |  |  | SCCP P6 - Dunedin Subtransmission network protection system upgrade |  | 2015-03-31: 95
|  |  |  | SCCP P7 - Aurora ICCP System |  | 2015-03-31: 55
|  |  |  | - Asbestos removal and refurbishment at South City and Corstorphine |  | 2015-03-31: 81
|  |  |  | Cast Iron Pothead replacement |  | 2015-03-31: 30
|  |  |  | Fire , Security, Earthquake & Asbestos Upgrades |  | 2015-03-31: 100
|  |  |  | ZS roof upgrade |  | 2015-03-31: 50
|  |  |  | Establish Earthing Points at Central zone substations |  |  | 4 | 2 | 2 | 1
|  |  |  | Improve Earth Fault Detection |  | 2016-03-31: 37; 2017-03-31: 0
|  |  |  | LV Service/Link Pillars (Central) |  |  | 15 | 19 | 19 | 18 | 18
|  |  |  | Mobile Generator (300kVA) |  | 2016-03-31: 184; 2017-03-31: 0
|  |  |  | Omakau Mobile Substation |  | 2016-03-31: 66
166 |  |  |  | Replace Alexandra Protection
167 |  |  |  | Replace Frankton Protection
168 |  |  |  | Replace Halfway Bush - Mosgiel - Waipori Protection
169 |  |  |  | Replacement of JW3 switchgear |  |  | 18 | 24 | 24 | 23 | 23
170 |  |  |  | *include additional rows if needed
171 |  |  |  | All other reliability, safety and environment projects or programmes
172 |  |  | Other reliability, safety and environment expenditure |  |  | 438.5 | 677 | 429 | 158 | 153 | 150 | [5 empty] | to row 40
173 |  | less |  | Capital contributions funding other reliability, safety and environment
174 |  |  | Other reliability, safety and environment less capital contributions |  |  | 438.5 | 677 | 429 | 158 | 153 | 150
175
176
177
178 | 11a(ix): Non-Network Assets
179 |  | Routine expenditure
180 |  |  |  | Project or programme*
181 |  |  |  | [Description of material project or programme]
182 |  |  |  | [Description of material project or programme]
183 |  |  |  | [Description of material project or programme]
184 |  |  |  | [Description of material project or programme]
185 |  |  |  | [Description of material project or programme]
186 |  |  |  | *include additional rows if needed
187 |  |  |  | All other routine expenditure projects or programmes
188 |  |  | Routine expenditure |  |  | 0 | 0 | 0 | 0 | 0 | 0
189 |  | Atypical expenditure
190 |  |  |  | Project or programme*
191 |  |  |  | [Description of material project or programme]
192 |  |  |  | [Description of material project or programme]
193 |  |  |  | [Description of material project or programme]
194 |  |  |  | [Description of material project or programme]
195 |  |  |  | [Description of material project or programme]
196 |  |  |  | *include additional rows if needed
197 |  |  |  | All other atypical projects or programmes
198 |  |  | Atypical expenditure |  |  | 0 | 0 | 0 | 0 | 0 | 0
199
200 |  |  | Non-network assets expenditure |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | to row 43

## S11b.Opex Forecast
[13 empty] | Company Name | Aurora Energy Limited
[13 empty] | AMP Planning Period | 42095 -1409d mmmm yyyy –45747 -1409d mmmm yyyy
SCHEDULE 11b: REPORT ON FORECAST OPERATIONAL EXPENDITURE
This schedule requires a breakdown of forecast operational expenditure for the disclosure year and a 10 year planning period. The forecasts should be consistent with the supporting information set out in the AMP. The forecast is to be expressed in both constant price and nominal dollar terms. EDBs must provide explanatory comment on the difference between constant price and nominal dollar operational expenditure forecasts in Schedule 14a (Mandatory Explanatory Notes). This information is not part of audited disclosure information.
sch ref
7 | [5 empty] | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | CY+9 | CY+10
8 |  |  |  |  | for year ended | 2015-03-31 | 2016-03-31 | 2017-03-31 | 2018-03-31 | 2019-03-31 | 2020-03-31 | 2021-03-31 | 2022-03-31 | 2023-03-31 | 2024-03-31 | 2025-03-31
9 |  | Operational Expenditure Forecast |  |  |  | 2015-03-31: $000 (in nominal dollars)
10 |  |  |  | Service interruptions and emergencies |  | 2746.5596 | 3155.6875 | 3187.3 | 3187.3 | 3187.3 | 3187.3 | 3187.3 | 3187.3 | 3187.3 | 3187.3 | 3187.3
11 |  |  |  | Vegetation management |  | 1906.5 | 4333.4388 | 4333.4388 | 4333.4388 | 4150.561 | 4089.6017 | 4089.6017 | 4089.6017 | 4089.6017 | 4089.6017 | 4089.6017
12 |  |  |  | Routine and corrective maintenance and inspection |  | 6160.1246 | 5589.3336 | 4999.5862 | 5309.2806 | 5147.3143 | 4585.9048 | 4795.5227 | 5146.3779 | 5209.3778 | 4935.0971 | 4455.5988
13 |  |  |  | Asset replacement and renewal |  | 430.1061 | 423.5 | 370.75 | 340.25 | 335.5 | 331.75 | 330.5 | 330.5 | 330.5 | 330.5 | 324.875
14 |  |  | Network Opex |  |  | 11243.2902 | 13501.9599 | 12891.075 | 13170.2694 | 12820.6753 | 12194.5565 | 12402.9244 | 12753.7796 | 12816.7795 | 12542.4988 | 12057.3754
15 |  |  |  | System operations and network support |  | 3857 | 3949.9348 | 4045.3369 | 4143.4119 | 4244.1598 | 4347.6886 | 4454.0644 | 4563.3655 | 4675.6724 | 4791.0678 | 4909.6365
16 |  |  |  | Business support |  | 2859.5 | 2928.3999 | 2999.1291 | 3071.8399 | 3146.5323 | 3223.2864 | 3302.1512 | 3383.1848 | 3466.4468 | 3551.9985 | 3639.9029
17 |  |  | Non-network opex |  |  | 6716.5 | 6878.3347 | 7044.466 | 7215.2518 | 7390.6921 | 7570.9749 | 7756.2155 | 7946.5503 | 8142.1192 | 8343.0663 | 8549.5394
18 |  |  | Operational expenditure |  |  | 17959.7902 | 20380.2946 | 19935.5409 | 20385.5211 | 20211.3674 | 19765.5314 | 20159.14 | 20700.3299 | 20958.8987 | 20885.5651 | 20606.9148
19 | [5 empty] | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | CY+9 | CY+10
20 |  |  |  |  | for year ended | 2015-03-31 | 2016-03-31 | 2017-03-31 | 2018-03-31 | 2019-03-31 | 2020-03-31 | 2021-03-31 | 2022-03-31 | 2023-03-31 | 2024-03-31 | 2025-03-31
21 | [5 empty] | 2015-03-31: $000 (in constant prices)
22 |  |  |  | Service interruptions and emergencies |  | 2746.5596 | 3096.8474 | 3063.5362 | 3003.4669 | 2944.5754 | 2886.8386 | 2830.2339 | 2774.7391 | 2720.3325 | 2666.9926 | 2614.6986
23 |  |  |  | Vegetation management |  | 1906.5 | 4252.6386 | 4165.17 | 4083.5 | 3834.4804 | 3704.0818 | 3631.4528 | 3560.2478 | 3490.439 | 3421.999 | 3354.901
24 |  |  |  | Routine and corrective maintenance and inspection |  | 6160.1246 | 5485.1164 | 4805.4508 | 5003.0585 | 4755.3273 | 4153.5993 | 4258.291 | 4480.236 | 4446.1581 | 4129.4725 | 3655.1464
25 |  |  |  | Asset replacement and renewal |  | 430.1061 | 415.6035 | 356.3537 | 320.6255 | 309.9504 | 300.4765 | 293.4748 | 287.7204 | 282.0788 | 276.5479 | 266.5109
26 |  |  | Network Opex |  |  | 11243.2902 | 13250.206 | 12390.5107 | 12410.6509 | 11844.3336 | 11044.9962 | 11013.4525 | 11102.9434 | 10939.0084 | 10495.012 | 9891.257
27 |  |  |  | System operations and network support |  | 3857 | 3902.6495 | 3928.2883 | 3936.9237 | 3952.4726 | 3968.101 | 3983.7998 | 3999.5693 | 4015.4097 | 4031.3214 | 4047.3047
28 |  |  |  | Business support |  | 2859.5 | 2893.3436 | 2912.3517 | 2918.7538 | 2930.2814 | 2941.868 | 2953.5068 | 2965.1979 | 2976.9417 | 2988.7383 | 3000.588
29 |  |  | Non-network opex |  |  | 6716.5 | 6795.9931 | 6840.64 | 6855.6776 | 6882.7539 | 6909.969 | 6937.3066 | 6964.7672 | 6992.3514 | 7020.0597 | 7047.8926
30 |  |  | Operational expenditure |  |  | 17959.7902 | 20046.199 | 19231.1507 | 19266.3285 | 18727.0875 | 17954.9652 | 17950.7591 | 18067.7106 | 17931.3598 | 17515.0717 | 16939.1496
31 |  | Subcomponents of operational expenditure (where known)
32 |  |  |  | Energy efficiency and demand side management, reduction of energy losses
33
34 |  |  |  | Direct billing*
35 |  |  |  | Research and Development
36 |  |  |  | Insurance
37 | * Direct billing expenditure by suppliers that direct bill the majority of their consumers
38
39 | [5 empty] | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | CY+9 | CY+10
40 |  |  |  |  | for year ended | 2015-03-31 | 2016-03-31 | 2017-03-31 | 2018-03-31 | 2019-03-31 | 2020-03-31 | 2021-03-31 | 2022-03-31 | 2023-03-31 | 2024-03-31 | 2025-03-31
41 |  | Difference between nominal and real forecasts |  |  |  | 2015-03-31: $000
42 |  |  |  | Service interruptions and emergencies |  | 0 | 58.8401 | 123.7638 | 183.8331 | 242.7246 | 300.4614 | 357.0661 | 412.5609 | 466.9675 | 520.3074 | 572.6014
43 |  |  |  | Vegetation management |  | 0 | 80.8001 | 168.2687 | 249.9387 | 316.0805 | 385.5199 | 458.1489 | 529.3539 | 599.1627 | 667.6027 | 734.7007
44 |  |  |  | Routine and corrective maintenance and inspection |  | 0 | 104.2172 | 194.1354 | 306.2221 | 391.987 | 432.3055 | 537.2317 | 666.1419 | 763.2197 | 805.6246 | 800.4524
45 |  |  |  | Asset replacement and renewal |  | 0 | 7.8965 | 14.3963 | 19.6245 | 25.5496 | 31.2735 | 37.0252 | 42.7796 | 48.4212 | 53.9521 | 58.3641
46 |  |  | Network Opex |  |  | 0 | 251.7539 | 500.5642 | 759.6185 | 976.3417 | 1149.5604 | 1389.4719 | 1650.8363 | 1877.7711 | 2047.4868 | 2166.1185
47 |  |  |  | System operations and network support |  | 0 | 47.2853 | 117.0486 | 206.4882 | 291.6873 | 379.5875 | 470.2645 | 563.7962 | 660.2627 | 759.7464 | 862.3318
48 |  |  |  | Business support |  | 0 | 35.0564 | 86.7774 | 153.0861 | 216.2509 | 281.4184 | 348.6444 | 417.9869 | 489.5051 | 563.2602 | 639.315
49 |  |  | Non-network opex |  |  | 0 | 82.3417 | 203.826 | 359.5742 | 507.9382 | 661.0059 | 818.9089 | 981.7831 | 1149.7678 | 1323.0066 | 1501.6468
50 |  |  | Operational expenditure |  |  | 0 | 334.0956 | 704.3903 | 1119.1927 | 1484.2798 | 1810.5662 | 2208.3808 | 2632.6194 | 3027.5389 | 3370.4934 | 3667.7653

## S12a.Asset Condition
[8 empty] | Company Name | Aurora Energy Limited
[8 empty] | AMP Planning Period | 42095 -1409d mmmm yyyy –45747 -1409d mmmm yyyy
SCHEDULE 12a: REPORT ON ASSET CONDITION
This schedule requires a breakdown of asset condition by asset class as at the start of the forecast year. The data accuracy assessment relates to the percentage values disclosed in the asset condition columns. Also required is a forecast of the percentage of units to be replaced in the next 5 years. All information should be consistent with the information provided in the AMP and the expenditure on assets forecast in Schedule 11a. All units relating to cable and line assets, that are expressed in km, refer to circuit lengths.
sch ref
7 |  |  |  |  | Asset condition at start of planning period (percentage of units by grade)
8 | [10 empty] | % of asset forecast to be replaced in next 5 years
9 | Voltage | Asset category | Asset class | Units | Grade 1 | Grade 2 | Grade 3 | Grade 4 | Grade unknown | Data accuracy (1–4)
10 | All | Overhead Line | Concrete poles / steel structure | No. | 0.7832% | 0.2204% | 30.65% | 68.34% | 0.009379% | 3 | 1.616%
11 | All | Overhead Line | Wood poles | No. | 6.719% | 7.363% | 67.34% | 18.52% | 0.06159% | 3 | 15.43%
12 | All | Overhead Line | Other pole types | No.
13 | HV | Subtransmission Line | Subtransmission OH up to 66kV conductor | km | 0% | 0% | 25.35% | 60.25% | 14.41% | 2 | 0.5069%
14 | HV | Subtransmission Line | Subtransmission OH 110kV+ conductor | km
15 | HV | Subtransmission Cable | Subtransmission UG up to 66kV (XLPE) | km | 0% | 0% | 0% | 99.02% | 0.9849% | 2 | 0%
16 | HV | Subtransmission Cable | Subtransmission UG up to 66kV (Oil pressurised) | km | 0% | 0% | 0% | 100% | 0% | 2 | 0%
17 | HV | Subtransmission Cable | Subtransmission UG up to 66kV (Gas pressurised) | km | 0% | 0% | 69.35% | 30.65% | 0% | 2 | 1.387%
18 | HV | Subtransmission Cable | Subtransmission UG up to 66kV (PILC) | km | 0% | 0% | 73.82% | 26.18% | 0% | 2 | 1.476%
19 | HV | Subtransmission Cable | Subtransmission UG 110kV+ (XLPE) | km
20 | HV | Subtransmission Cable | Subtransmission UG 110kV+ (Oil pressurised) | km
21 | HV | Subtransmission Cable | Subtransmission UG 110kV+ (Gas Pressurised) | km
22 | HV | Subtransmission Cable | Subtransmission UG 110kV+ (PILC) | km
23 | HV | Subtransmission Cable | Subtransmission submarine cable | km
24 | HV | Zone substation Buildings | Zone substations up to 66kV | No. | 3.571% | 0% | 28.57% | 67.86% | 0% | 3 | 4.143%
25 | HV | Zone substation Buildings | Zone substations 110kV+ | No.
26 | HV | Zone substation switchgear | 22/33kV CB (Indoor) | No. | 0% | 0% | 0% | 100% | 0% | 3 | 0%
27 | HV | Zone substation switchgear | 22/33kV CB (Outdoor) | No. | 0% | 0% | 23.26% | 39.53% | 37.21% | 2 | 0.4651%
28 | HV | Zone substation switchgear | 33kV Switch (Ground Mounted) | No.
29 | HV | Zone substation switchgear | 33kV Switch (Pole Mounted) | No. | 0.4695% | 0.4695% | 17.84% | 42.25% | 38.97% | 2 | 1.296%
30 | HV | Zone substation switchgear | 33kV RMU | No.
31 | HV | Zone substation switchgear | 50/66/110kV CB (Indoor) | No.
32 | HV | Zone substation switchgear | 50/66/110kV CB (Outdoor) | No. | 0% | 0% | 0% | 100% | 0% | 2 | 0%
33 | HV | Zone substation switchgear | 3.3/6.6/11/22kV CB (ground mounted) | No. | 4.72% | 7.375% | 11.21% | 39.23% | 37.46% | 2 | 12.32%
34 | HV | Zone substation switchgear | 3.3/6.6/11/22kV CB (pole mounted) | No. | 0% | 0% | 10.53% | 31.58% | 57.89% | 2 | 0.2105%
42 |  |  |  |  | Asset condition at start of planning period (percentage of units by grade)
43 | [10 empty] | % of asset forecast to be replaced in next 5 years
44 | Voltage | Asset category | Asset class | Units | Grade 1 | Grade 2 | Grade 3 | Grade 4 | Grade unknown | Data accuracy (1–4)
45 | HV | Zone Substation Transformer | Zone Substation Transformers | No. | 0% | 7.576% | 37.88% | 43.94% | 10.61% | 2 | 8.333%
46 | HV | Distribution Line | Distribution OH Open Wire Conductor | km | 0.9014% | 3.123% | 33.06% | 43.61% | 19.3% | 2 | 4.686%
47 | HV | Distribution Line | Distribution OH Aerial Cable Conductor | km
48 | HV | Distribution Line | SWER conductor | km | 0% | 0% | 23.03% | 12.65% | 64.32% | 2 | 0.4606%
49 | HV | Distribution Cable | Distribution UG XLPE or PVC | km | 0% | 0% | 1.429% | 98.52% | 0.05213% | 1 | 0.02857%
50 | HV | Distribution Cable | Distribution UG PILC | km | 0% | 1.698% | 16.68% | 81.32% | 0.2985% | 1 | 2.032%
51 | HV | Distribution Cable | Distribution Submarine Cable | km | 0% | 0% | 0% | 0% | 100% | 1 | 0%
52 | HV | Distribution switchgear | 3.3/6.6/11/22kV CB (pole mounted) - reclosers and sectionalisers | No. | 0% | 0% | 17.39% | 82.61% | 0% | 3 | 0.3478%
53 | HV | Distribution switchgear | 3.3/6.6/11/22kV CB (Indoor) | No. | 0% | 0% | 12.5% | 37.5% | 50% | 2 | 0.25%
54 | HV | Distribution switchgear | 3.3/6.6/11/22kV Switches and fuses (pole mounted) | No. | 0.934% | 2.634% | 34.54% | 35.86% | 26.03% | 2 | 4.258%
55 | HV | Distribution switchgear | 3.3/6.6/11/22kV Switch (ground mounted) - except RMU | No. | 2.268% | 0.907% | 12.93% | 51.02% | 32.88% | 2 | 3.433%
56 | HV | Distribution switchgear | 3.3/6.6/11/22kV RMU | No. | 13.04% | 0.7246% | 32.61% | 53.62% | 0% | 2 | 14.42%
57 | HV | Distribution Transformer | Pole Mounted Transformer | No. | 1.612% | 3.778% | 22.52% | 37.63% | 34.46% | 2 | 5.84%
58 | HV | Distribution Transformer | Ground Mounted Transformer | No. | 2.149% | 1.922% | 13.12% | 73.69% | 9.122% | 3 | 4.333%
59 | HV | Distribution Transformer | Voltage regulators | No. | 0% | 0% | 3.448% | 93.1% | 3.448% | 2 | 0.06897%
60 | HV | Distribution Substations | Ground Mounted Substation Housing | No. | 0% | 0% | 100% | 0% | 0% | 3 | 2%
61 | LV | LV Line | LV OH Conductor | km | 1.236% | 2.851% | 38.52% | 42.09% | 15.3% | 2 | 4.857%
62 | LV | LV Cable | LV UG Cable | km | 0.3174% | 0.8198% | 11.2% | 85.55% | 2.11% | 1 | 1.361%
63 | LV | LV Streetlighting | LV OH/UG Streetlight circuit | km | 1.522% | 2.49% | 30.52% | 47.15% | 18.32% | 2 | 4.622%
64 | LV | Connections | OH/UG consumer service connections | No. | 0.7285% | 1.638% | 10.92% | 48.27% | 38.44% | 1 | 2.585%
65 | All | Protection | Protection relays (electromechanical, solid state and numeric) | No. | 3.39% | 5.297% | 12.71% | 45.13% | 33.47% | 3 | 8.941%
66 | All | SCADA and communications | SCADA and communications equipment operating as a single system | Lot | 25% | 25% | 42% | 8% |  | 3 | 50%
67 | All | Capacitor Banks | Capacitors including controls | No. | 0% | 25% | 70% | 5% |  | 3 | 16.67%
68 | All | Load Control | Centralised plant | Lot | 25% | 35% | 35% | 5% |  | 3 | 25%
69 | All | Load Control | Relays | No. | 1.68% | 2.407% | 23.98% | 61.9% | 10.04% | 3 | 4.567%
70 | All | Civils | Cable Tunnels | km

## S12b.Capacity Forecast
[11 empty] | Company Name | Aurora Energy Limited
[11 empty] | AMP Planning Period | 42095 -1409d mmmm yyyy –45747 -1409d mmmm yyyy
SCHEDULE 12b: REPORT ON FORECAST CAPACITY
This schedule requires a breakdown of current and forecast capacity and utilisation for each zone substation and current distribution transformer capacity. The data provided should be consistent with the information provided in the AMP. Information provided in this table should relate to the operation of the network in its normal steady state configuration.
sch ref
7 | 12b(i): System Growth - Zone Substations
8 |  |  | Existing Zone Substations | Current Peak Load (MVA) | Installed Firm Capacity (MVA) | Security of Supply Classification (type) | Transfer Capacity (MVA) | Utilisation of Installed Firm Capacity % | Installed Firm Capacity +5 years (MVA) | Utilisation of Installed Firm Capacity + 5yrs % | Installed Firm Capacity Constraint +5 years (cause) | Explanation
9 |  |  | Alexandra | 10.7 | 15 | n-1 | 0 | 71.33% | 15 | 72.23% | No constraint within +5 years
10 |  |  | Anderson’s Bay | 14.5 | 18 | n-1 | 5 | 80.56% | 18 | 85.1% | No constraint within +5 years
11 |  |  | Arrowtown | 7.9 | 7.5 | n-1 | 2 | 105.3% | 24 | 40% | No constraint within +5 years | Upgrade planned 2018-2019
12 |  |  | Berwick | 1.4 | 3.6 | n | 4 | 38.89% | 3.6 | 43.1% | No constraint within +5 years
13 |  |  | Cardrona | 3.3 | 5 | n | 5 | 66% | 5 | 59.66% | No constraint within +5 years
14 |  |  | Clyde/Earnscleugh | 4.2 | 4.8 | n-1 | 1 | 87.5% | 4.8 | 91.85% | No constraint within +5 years
15 |  |  | Commonage | 10.2 | 23 | n-1 | 6 | 44.35% | 23 | 51.15% | No constraint within +5 years
16 |  |  | Coronet Peak | 5.4 | 6 | n | 0 | 90% | 6 | 90.49% | No constraint within +5 years
17 |  |  | Corstorphine | 12.5 | 23 | n-1 | 6 | 54.35% | 23 | 54.95% | No constraint within +5 years
18 |  |  | Cromwell | 10.7 | 9 | n-1 | 0 | 118.9% | 24 | 49.2% | No constraint within +5 years | Upgrade Planned 2017-2018
19 |  |  | Dalefield | 2.8 | 3.6 | n | 1 | 77.78% | 3.6 | 94.62% | No constraint within +5 years
20 |  |  | East Taieri | 15.9 | 24 | n-1 | 4 | 66.25% | 24 | 70.53% | No constraint within +5 years
21 |  |  | Ettrick | 1.7 | 3.6 | n | 2 | 47.22% | 3.6 | 53.19% | No constraint within +5 years
22 |  |  | Frankton | 13 | 17 | n-1 | 6 | 76.47% | 17 | 91.04% | No constraint within +5 years
23 |  |  | Fernhill | 6.3 | 10 | n-1 | 4 | 63% | 10 | 64.87% | No constraint within +5 years
24 |  |  | Green Island | 13.3 | 18 | n-1 | 6 | 73.89% | 18 | 74.17% | No constraint within +5 years
25 |  |  | Halfway Bush | 14.1 | 18 | n-1 | 6 | 78.33% | 18 | 84.51% | No constraint within +5 years
26 |  |  | Kaikorai Valley | 10.6 | 23 | n-1 | 4 | 46.09% | 23 | 47.27% | No constraint within +5 years
27 |  |  | Lindis Crossing | 0 | 7.5 | n | 7.5 | 0% | 7.5 | 66.62% | No constraint within +5 years
|  |  | Maungawera /Camphill | 4 | 3.3 | n | 2 | 121.2% | 8 | 56% | No constraint within +5 years | Upgrade planned 2015
28 |  |  | Mosgiel | 7.1 | 14 | n-1 | 2 | 50.71% | 14 | 51.58% | No constraint within +5 years
|  |  | Neville St | 13.1 | 18 | n-1 | 6 | 72.78% | 24 | 55% | No constraint within +5 years | Upgrade planned 2016
|  |  | North City | 19.1 | 28 | n-1 | 6 | 68.21% | 28 | 67.6% | No constraint within +5 years
|  |  | North East Valley | 11.1 | 23 | n-1 | 4 | 48.26% | 23 | 50.95% | No constraint within +5 years
|  |  | Omakau | 2.8 | 3.6 | n | 1 | 77.78% | 8 | 47.77% | No constraint within +5 years | Upgrade planned 2016
|  |  | Outram | 2.7 | 5.6 | n-1 | 2 | 48.21% | 5.6 | 53.29% | No constraint within +5 years
|  |  | Port Chalmers | 7 | 10 | n-1 | 3 | 70% | 10 | 69.45% | No constraint within +5 years
|  |  | Queensberry | 7 | 3.3 | n | 1 | 212.1% | 4 | 82.79% | No constraint within +5 years | Load transferred to new Lindis Crossing substation
|  |  | Queenstown | 13.6 | 26 | n-1 | 6 | 52.31% | 26 | 58.49% | No constraint within +5 years
|  |  | Remarkables | 1.9 | 3.6 | n | 0 | 52.78% | 6 | 79.17% | No constraint within +5 years
|  |  | Roxburgh | 1.8 | 6 | n | 1 | 30% | 6 | 30.14% | No constraint within +5 years
|  |  | Smith St | 15.5 | 18 | n-1 | 6 | 86.11% | 18 | 91.97% | No constraint within +5 years
|  |  | South City | 14.9 | 18 | n-1 | 6 | 82.78% | 18 | 84.56% | No constraint within +5 years
|  |  | St Kilda | 15.5 | 23 | n-1 | 6 | 67.39% | 23 | 65.79% | No constraint within +5 years
|  |  | Wanaka | 18.8 | 24 | n-1 | 1 | 78.33% | 24 | 94.79% | No constraint within +5 years
|  |  | Ward St | 12.8 | 24 | n-1 | 6 | 53.33% | 24 | 59.05% | No constraint within +5 years
|  |  | Willowbank | 12.3 | 18 | n-1 | 4 | 68.33% | 18 | 68.32% | No constraint within +5 years
29 |  |  | ¹ Extend forecast capacity table as necessary to disclose all capacity by each zone substation
30 | 12b(ii): Transformer Capacity
31 |  |  |  | (MVA)
32 |  |  | Distribution transformer capacity (EDB owned)
33 |  |  | Distribution transformer capacity (Non-EDB owned)
34 |  | Total distribution transformer capacity |  | 0
35
36 |  | Zone substation transformer capacity

## S12c.Demand Forecast
[8 empty] | Company Name | Aurora Energy Limited
[8 empty] | AMP Planning Period | 42095 -1409d mmmm yyyy –45747 -1409d mmmm yyyy
SCHEDULE 12C: REPORT ON FORECAST NETWORK DEMAND
This schedule requires a forecast of new connections (by consumer type), peak demand and energy volumes for the disclosure year and a 5 year planning period. The forecasts should be consistent with the supporting information set out in the AMP as well as the assumptions used in developing the expenditure forecasts in Schedule 11a and Schedule 11b and the capacity and utilisation forecasts in Schedule 12b.
sch ref
7 | 12c(i): Consumer Connections
8 |  |  | Number of ICPs connected in year by consumer type |  |  | Number of connections
9 | [5 empty] | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5
10 |  |  |  |  | for year ended | 2015-03-31 | 2016-03-31 | 2017-03-31 | 2018-03-31 | 2019-03-31 | 2020-03-31
11 |  |  |  | Consumer types defined by EDB*
12 |  |  |  | Standard Domestic 8kVA |  | 700 | 733 | 753 | 772 | 792 | 812
|  |  |  | Standard Domestic 15kVA |  | 70927 | 71952 | 72698 | 73444 | 74189 | 74935
|  |  |  | Load Group 0 |  | 360 | 369 | 378 | 387 | 395 | 403
|  |  |  | Load Group 0A |  | 516 | 428 | 423 | 418 | 414 | 409
|  |  |  | Load Group 1A |  | 801 | 884 | 931 | 977 | 1024 | 1069
|  |  |  | Load Group 1 |  | 5632 | 5446 | 5399 | 5353 | 5306 | 5259
|  |  |  | Load Group 2 |  | 6024 | 6318 | 6467 | 6617 | 6767 | 6917
|  |  |  | Load Group 3 |  | 192 | 198 | 200 | 202 | 204 | 206
13 |  |  |  | Load Group 3A |  | 153 | 161 | 164 | 166 | 168 | 169
14 |  |  |  | Load Group 4 |  | 110 | 121 | 123 | 127 | 130 | 134
15 |  |  |  | Load Group 5 |  | 9 | 8 | 8 | 8 | 8 | 7
16 |  |  |  | Street Lighting |  | 11 | 13 | 14 | 14 | 15 | 15
17 |  |  | Connections total |  |  | 85435 | 86631 | 87558 | 88485 | 89412 | 90335
18 |  |  |  | *include additional rows if needed
19 |  | Distributed generation
20 |  |  |  | Number of connections |  | 102 | 118 | 133 | 149 | 164 | 180
21 |  |  |  | Installed connection capacity of distributed generation (MVA) |  | 2288 | 2120 | 1953 | 1785 | 1617 | 1450
22 | 12c(ii) System Demand
23 | [5 empty] | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5
24 |  | Maximum coincident system demand (MW) |  |  | for year ended | 2015-03-31 | 2016-03-31 | 2017-03-31 | 2018-03-31 | 2019-03-31 | 2020-03-31
25 |  |  |  | GXP demand |  | 226.269 | 226.5843 | 226.8987 | 227.2131 | 227.5276 | 227.8437
26 |  | plus |  | Distributed generation output at HV and above |  | 56.7331 | 56.8122 | 56.891 | 56.9699 | 57.0487 | 57.128
27 |  |  | Maximum coincident system demand |  |  | 283.0022 | 283.3965 | 283.7898 | 284.183 | 284.5762 | 284.9717
28 |  | less |  | Net transfers to (from) other EDBs at HV and above
29 |  |  | Demand on system for supply to consumers' connection points |  |  | 283.0022 | 283.3965 | 283.7898 | 284.183 | 284.5762 | 284.9717
30 |  | Electricity volumes carried (GWh)
31 |  |  |  | Electricity supplied from GXPs |  | 1075.005 | 1081.8424 | 1093.6604 | 1100.527 | 1107.4075 | 1114.3122
32 |  | less |  | Electricity exports to GXPs |  | 45 | 45 | 45 | 45 | 45 | 45
33 |  | plus |  | Electricity supplied from distributed generation |  | 312.6667 | 312.6667 | 312.6667 | 312.6667 | 312.6667 | 312.6667
34 |  | less |  | Net electricity supplied to (from) other EDBs | bar: 2015-03-31 to 2020-03-31
35 |  |  | Electricity entering system for supply to ICPs |  |  | 1343.6717 | 1350.509 | 1362.327 | 1369.1937 | 1376.0741 | 1382.9788
36 |  | less |  | Total energy delivered to ICPs |  | 1265.7387 | 1272.1795 | 1284.6744 | 1291.1497 | 1297.6379 | 1304.149
37 |  |  | Losses |  |  | 77.933 | 78.3295 | 77.6526 | 78.044 | 78.4362 | 78.8298
38
39 |  |  | Load factor |  |  | 54.2% | 54.4% | 54.8% | 55% | 55.2% | 55.4%
40 |  |  | Loss ratio |  |  | 5.8% | 5.8% | 5.7% | 5.7% | 5.7% | 5.7%

## S12d.Reliability Forecast (Tot)
[6 empty] | Company Name | Aurora Energy Limited
[6 empty] | AMP Planning Period | 42095 -1409d mmmm yyyy –45747 -1409d mmmm yyyy
[6 empty] | Network / Sub-network Name | Total Network
SCHEDULE 12d: REPORT FORECAST INTERRUPTIONS AND DURATION
This schedule requires a forecast of SAIFI and SAIDI for disclosure and a 5 year planning period. The forecasts should be consistent with the supporting information set out in the AMP as well as the assumed impact of planned and unplanned SAIFI and SAIDI on the expenditures forecast provided in Schedule 11a and Schedule 11b.
sch ref
8 |  |  |  | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5
9 |  |  | for year ended | 2015-03-31 | 2016-03-31 | 2017-03-31 | 2018-03-31 | 2019-03-31 | 2020-03-31
10 | SAIDI
11 |  | Class B (planned interruptions on the network) |  | 19.63 | 7.055 | 7.055 | 7.055 | 7.055 | 7.055
12 |  | Class C (unplanned interruptions on the network) |  | 102.61 | 76.31 | 76.31 | 76.31 | 76.31 | 76.31
13 | SAIFI
14 |  | Class B (planned interruptions on the network) |  | 0.105 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047
15 |  | Class C (unplanned interruptions on the network) |  | 1.287 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4

## S12d.Reliability Forecast (Dn)
[6 empty] | Company Name | Aurora Energy Limited
[6 empty] | AMP Planning Period | 42095 -1409d mmmm yyyy –45747 -1409d mmmm yyyy
[6 empty] | Network / Sub-network Name | Dunedin
SCHEDULE 12d: REPORT FORECAST INTERRUPTIONS AND DURATION
This schedule requires a forecast of SAIFI and SAIDI for disclosure and a 5 year planning period. The forecasts should be consistent with the supporting information set out in the AMP as well as the assumed impact of planned and unplanned SAIFI and SAIDI on the expenditures forecast provided in Schedule 11a and Schedule 11b.
sch ref
8 |  |  |  | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5
9 |  |  | for year ended | 2015-03-31 | 2016-03-31 | 2017-03-31 | 2018-03-31 | 2019-03-31 | 2020-03-31
10 | SAIDI
11 |  | Class B (planned interruptions on the network) |  | 2.84 | 1.616 | 1.616 | 1.616 | 1.616 | 1.616
12 |  | Class C (unplanned interruptions on the network) |  | 60.25 | 34.287 | 34.287 | 34.287 | 34.287 | 34.287
13 | SAIFI
14 |  | Class B (planned interruptions on the network) |  | 0.016 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013
15 |  | Class C (unplanned interruptions on the network) |  | 0.726 | 0.596 | 0.596 | 0.596 | 0.596 | 0.596

## S12d.Reliability Forecast (CO)
[6 empty] | Company Name | Aurora Energy Limited
[6 empty] | AMP Planning Period | 42095 -1409d mmmm yyyy –45747 -1409d mmmm yyyy
[6 empty] | Network / Sub-network Name | Central Otago
SCHEDULE 12d: REPORT FORECAST INTERRUPTIONS AND DURATION
This schedule requires a forecast of SAIFI and SAIDI for disclosure and a 5 year planning period. The forecasts should be consistent with the supporting information set out in the AMP as well as the assumed impact of planned and unplanned SAIFI and SAIDI on the expenditures forecast provided in Schedule 11a and Schedule 11b.
sch ref
8 |  |  |  | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5
9 |  |  | for year ended | 2015-03-31 | 2016-03-31 | 2017-03-31 | 2018-03-31 | 2019-03-31 | 2020-03-31
10 | SAIDI
11 |  | Class B (planned interruptions on the network) |  | 50.62 | 38.18 | 38.18 | 38.18 | 38.18 | 38.18
12 |  | Class C (unplanned interruptions on the network) |  | 175.61 | 132.467 | 132.467 | 132.467 | 132.467 | 132.467
13 | SAIFI
14 |  | Class B (planned interruptions on the network) |  | 0.257 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32
15 |  | Class C (unplanned interruptions on the network) |  | 2.227 | 2.779 | 2.779 | 2.779 | 2.779 | 2.779